## BOQ (ACADEMIC BLOCK)
ITEM NO. | DESCRIPTION OF ITEM | UNIT | QUANTITY (ACADEMIC BLOCK ) | RATE (INR) | AMOUNT (INR)
CLADDING / WALL LINING WORKS
| Providing and fixing 2nd class teak wood corner beading of triangular shape and size 50x50 mm (base and height) moulded to the junction of paneling, edgings, margins etc. fixed in position with rawl plugs, nails etc. as required and priming coat on unexposed surface complete with rubbing, polishing etc. as per the direction of Engineer in Charge. | Meter | 10
1 | Providing and fixing 2nd class teak wood moulded beading of approved shape and size to door, window and partition frames with iron screws, plugs and priming coat on unexposed surface etc. all complete. | Cum | 0.25
2 | Providing and fixing carbon steel galvanised ( minimum coating 5 micron) dash fastener of 10 mm dia double threaded 6.8 grade (yield strength 480 N/mm2), counter sunk head, comprising of 10 mm dia polyamide PA 6 grade sleeve, including drilling of hole in frame , concrete/ masonry, etc. as per direction of Engineer-in-charge.
a | 10x120 mm | Each | 25
b | 10x140 mm | Each | 25
TOTAL SUB HEAD
PARTITION & PANELLING
3 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/ sqm(both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre.
The boards are to be fixed to the frame work with joints staggered to avoid through cracks, Galvanised M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each with zinc coating of 120 gms/sqm(both side inclusive)) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete.
| 75 mm overall thickness partition with 12.5 mm thick double skin fire rated Glass Reinforced Gypsum (GRG) board conforming to IS: 2095: (part 3) : 1996 (Board with BIS certification marks) | Sqm | 5
4 | GI frame work for Partition/Panelling Providing and fixing GI frame work for partition/panelling upto true ceiling height consisting of G.I. frame , including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/ sqm(both side inclusive), consisting of floor and ceiling channel 72mm wide having equal flanges of 30 mm and 0.55 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 70 mm wide having one flange of 34 mm and other flange 36 mm and 0.55 mm thick fixed vertically within flanges of floor and ceiling channel at true ceiling level and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, including providing Galvanised M.S. fixing channel / Noggin channel of 70mm width (0.5mm thick having two flanges of 40mm mm each zinc coating of 120gms/Sqm (both side inclusive) shall be provided horizontally @ 600mm c/c with the help of 4.2x13mm wafer head metal to metal screws, make of partition framing. | Sqm | 5
| Providing and fixing thermal insulation with Resin Bonded Fibre glass wool conforming to IS: 8183 having density 32kg/m3, 50mm thick, wrapped in 200G Virgin Polythene Bags fixed to wall with screw, rawel plug & washers and held in position by criss crossing GI wire etc. complete as per directions of Engineer-in-Charge. | sqm | 248
5 | Providing and fixing frame work for partitions/ wall lining etc. made of 50x25x1.25mm / as approved, hollow MS tube, placed along the walls, ceiling and floor in a grid pattern with spacing @ 60 cm centre to centre both ways (vertically & horizontally) or at required spacing near opening, with necessary welding at junctions and fixing the frame to wall/ ceiling/ floors with steel dash fasteners of 8 mm dia, 75 mm long bolt, including making provision for opening for doors, windows, electrical conduits, switch boards etc., including providing with two coats of approved steel primer etc. complete, all as per direction of Engineer-in-charge. | kg | 30264
6 | Providing and fixing plain lining with necessary screws/nuts & bolts/ nails, including a coat of approved primer on one face, and fixed on wooden /steel frame work, complete as per direction of Engineer-incharge (Frame work shall be paid for separately).
| 12mm thick BWP Grade Ply | sqm | 10
| 19mm thick BWP Grade Ply | sqm | 10
7 | Providing & Fixing decorative high pressure laminated sheet of plain / wood grain in gloss / matt/ suede finish with high density protective surface layer and reverse side of adhesive bonding quality conforming to IS : 2046 Type S, including cost of adhesive of approved quality.
| 1.0 mm thick ( Basic Rate is Rs. 323.00 / Sqm) | Sqm | 3647
8 | Providing and fixing plywood of 4mm thick, one side decorative veneer conforming to IS: 1328 (type-1), for plain lining / cladding with necessary screws, including priming coat on unexposed surface with : MS framework shall be paid separatley.
| Decorative veneer facings of approved manufacture (Basic Cost is Rs.850 / Sqm) | sqm | 5
9 | Providing and fixing plain Gypsum board with necessary screws, including a coat of approved primer on one face, and fixed on GI/steel frame work, complete as per direction of Engineer-incharge (Frame work shall be paid for separately), The boards are to be fixed to the frame work with joints staggered to avoid through cracks, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape,joint finisher as per manufacture's specification and direction of engineer in charge all complete.
| 12.5 mm thick tapered edged plain Gypsum plaster board conforming to IS: 2095: (part I): 2011 (Board with BIS certification marks) | sqm | 5
10 | Providing and fixing 6mm thick lacquered glass of approved make on wall panelling over 12mm thick marine plywood/BWP ply base (conforming to IS : 710) fixed over MS frame work. Glass shall be fixed with clear neutral silicon of make GE winsil 20/ silpruf or DOW CORNING 995 over plywood complete as per detail in drawing and directions of Engineer-in-charge. Plywood cost is included in this item. MS Frame work will be paid separately. | Sqm | 46
11 | Providing and fixing 6mm thick lacquered glass fixed with 50X10mm ss studs of approved make on wall panelling over 12mm thick marine plywood/BWP ply base (conforming to IS : 710) fixed over MS frame work. Glass shall be fixed with clear neutral silicon of make GE winsil 20/ silpruf or DOW CORNING 995 over plywood complete as per detail in drawing and directions of Engineer-in-charge. Plywood cost is included in this item. MS Frame work will be paid separately. | Sqm | 24
12 | Providing and fixing 100 mm high Stainless steel sheet skirting made out of 1.2mm thick Stainless steel sheet SS304 moulded to profile inc sections fixed over 12mm thick marine ply using epoxy adhesives, fixing with screws, rubber beading etc.),polishing etc , cutting, bending, curing etc all complete. | Metre | 5
13 | Providing and fixing 6 mm thick marine plywood (conforming to IS: 710) skirting using epoxy adhesives, fixing with screws, etc on partition wall or required location, including a coat of approved primer on one face, as per drawing and directions of Engineer-in-charge | Sqm | 5
14 | Providing and fixing 8 mm thick marine plywood (conforming to IS: 710) skirting using epoxy adhesives, fixing with screws, etc on partition wall or required location, including a coat of approved primer on one face, as per drawing and directions of Engineer-in-charge | Sqm | 5
15 | Providing and fixing 10 mm thick marine plywood (conforming to IS: 710) skirting using epoxy adhesives, fixing with screws, etc on partition wall or required location, including a coat of approved primer on one face, as per drawing and directions of Engineer-in-charge | Sqm | 5
16 | Providing and fixing 12 mm thick marine plywood (conforming to IS: 710) skirting using epoxy adhesives, fixing with screws, etc on partition wall or required location, including a coat of approved primer on one face, as per drawing and directions of Engineer-in-charge | Sqm | 4656
17 | ACOUSTIC FABRIC PANELLING Supply and Installation of Soak Cord, kerfed edge, fabric wrapped magnesite bonded 2mm wide pinewood fibre core panel ,GreenPro certified,of size 600x2400x25mm, with ribbed finish, volume density 400Kgs/m3, weight 10 kg/m2 installed by using Strut framework system with Strut H-Spline. "The Strut framework systems includes Strut CC25 thickness 0.55mm, length 3600mm, knurled web 50mm, depth 25mm and equal flanges 15mm is fastened to wall positioned horizontally in a regular manner at 600mm centres. Strut H-Spline having sectional thickness 2mm and length 2400mm to be fixed perpendicular to the Strut CC25 at 600mm centers. Soak cord, Kerfed edge panels shall then be inserted into the Strut H-Spline along their long edges to perfect fit with staggered short edges. Note: Thickness is for bare panels. Add 4mm for Cord fabric. (Fabric colour as per architect's choice from currently valid swatch card)" The system is backlined with the acoustical infill SynthPF 10x25 adhered on wall with dab spots of Stick S7. Technical Parameters "• Fire (Class) – 1 & P • Acoustics – NRC 0.75 (For 20mm thk C25 mounting) upto 0.8 (for 25mm thk, C25 Mounting) • Thermal (W/mk)– 0.07 • Climate (°C, RH) – 50, 95 • Light (%) – Colour Dependant • Green (VoC, RC %) – Low, 30" | Sqm | 927
18 | GLASS PARTTION Providing and fixing slim frame System for Glass Partition(Fixed Glass Partition with 10mm Glass) Sleek Partition of aluminium profile with Clip-on / U-Section of size 30mm x 21mm with 2.5mm Wall thickness in matt black/ Natural Alu finish. Partition to be provided with suitable gaskets for insertion of 10mm thick clear toughened glass. Partition Glass joineries consists of two-way Polycarbonate I-profiles, 90 Degree Polycarbonate L-Junction and Polycarbonate T-Junction profiles. Polycarbonate profile joineries to be fixed with double sided adhesive tape & profiles to be inserted in the joint instead of sealing it with sealants. Polycarbonate profiles to be used at glass to glass joineries to give continuity glass effect. Hardware for fixing profiles to be used as per manufacturer standard. Costs should be inclusive of necessary Hardware for fixing of profiles & installation charges. SINGLE GLAZED FIXED PARTITION WITH 10MM GLASS | Sqm | 54
19 | Supply & Installation of 1 mm thick Stainless Steel, Grade-304 sheet cladding pasted using chemical adhesive over 2 layers of 6 mm thick water tight commercial flexi ply fixed over frame of 25x50 mm anticorrosive mild steel lincluding providing grooves as per design in mat/glossy/hairline finish complete | Sqm | 5
20 | Supply & Installation of 1 mm thick Stainless Steel, Grade-304 sheet cladding pasted using chemical adhesive over 2 layers of 6 mm thick water tight commercial flexi ply lincluding providing grooves as per design in mat/glossy/hairline finish complete | Sqm | 5
21 | 9.105 Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/sqm(both side inclusive), consisting of floor and ceiling channel 50 mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete.
| 9.105.1 75 mm overall thickness partition with 12.5 mm thick double skin fire rated Glass Reinforced Gypsum (GRG) plaster board conforming to IS: 2095: part 3 (Board with BIS certification marks) | Sqm | 10
22 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top pivot & top & bottom patch fitting , pivot & double action hydraulic floor spring type fixing arrangement and making necessary holes etc. for fixing required door fittings, all complete as per direction of Engineer-incharge (Including Door handle, lock and stopper etc.) | Sqm | 4.8
23 | Providing, supplying and fixing glazing upto ceiling height using 12mm clear toughened glass of approved make fixed to the floor, ceiling and sides with embedded aluminium U channel of required size including EPDM pad/ backer rod and structural / weather glass silicon sealant to make the glazing air and water tight including neatly cutting the chase in flooring/ cladding, embedding the U channel and making the same good and fixing to MS frame work at ceiling level etc. all complete as per drawings, specifications and directions of Engineer in charge. ( MS framework shall be paid separately) | Sqm | 5
24 | Providing and fixing self adhesive type frosted glass film of 3M make or approved equivalent, in required pattern over glass etc. as per drawings, including cleaning the receiving surface of glass etc., all complete as per manufacturer's specification and direction of Engineer in charge, bubble-free installation to be done on clean glass by Authorized Installers of 3M/approved make having Certificate of image license and shall provide Warranty for a period of 5 years, all complete as per direction of Enigneer In Charge
24.1 | Plain frosted/dusted film | Sqm | 94.6
24.2 | Digitally Printed frosted film | Sqm | 412
25 | Providing & Fixing Film (Shade Number) a flexible cast PVC with Comply™ adhesive intended to cover all type of the surfaces, such as wall covering, fur-niture, fixture, ceiling, doors, elevators, exterior/interior applications. Film – approx. 215 microns (film/adhesive) PVC, cadmium-free. Thickness will vary between designs,Adhesive would be Permanent acrylic adhesive with Comply™ performance & a Liner of PE coated Kraft paper. Contractors payment wouldn't be released until & unless he/she produces orginal warranty letter from the (3M) manufacturer. | Sqm | 10
26 | Providing & fixing Decorative / Privacy Glazing Film with the following features backed by manufacturers MCS warranty of 5 years.The material should consist of a durable polyester with a decorative matte surface, manufactured with a silicone liner to protect clear pressure-sensitive adhesive. Films contain no metals, but so contain infrared-absorbing carbon, metal oxide particles, or both. Film should have nominal thickness of between 3.0 mils and 3.5 mils (0.003 and 0.0035 inches).The film color should be clear, containing no metal coatings or dyed polyesters. 1. Ultraviolet Rejected : Not less than 99 percent. 2. Visible Light Transmission : Not more than 49 percent. 3. Visible Light Rejected: Not less than 19 percent. 4. Solar Heat Reduction: Not less than 14 percent. 5. Shading Coefficient at 90 Degrees (Normal Incidence) (ASTM E 903): Not less than 0.62. Backed by MCS warranty for 5Years from ARCHITECTURAL MARKET DEPARTMENT. | Sqm | 189.2
27 | Supply & Installation of Clear view Décor (IJ8150 Optically Clear Film along with IJ8150 overlaminate with Custom Printing ) or approved equivalent, with approved artwork digitally reproduced with water-based inks certified to have no hazardous air pollutant, selfadhesive, optically clear, bubble-free installation to be done on clean glass by Authorized Installers of /approved make having Certificate of image license and shall provide Warranty for a period of 5 years, all complete as per direction of Enigneer In Charge (Basic Rate is Rs. 3300 per Sqm) | Sqm | 54
| Providing & Fixing Digitally reproduced decorative graphics on IJ180C (with controltac & comply feature for direct, bubble-free application on walls) with UV protective matte overlaminate 8520 with a polyethylene-coated paper liner. Customised imagery & the thickness of 2 mil (0.05mm) without adhesive & 3-4mil (0.8-0.10mm) with adhesive, having minimum tensile strength of 5 pounds/inch at 73°F (0.9 kg/cm at 23°C ). the adhesive should be Pressure activated, positionable, with air release channels. MCS warranty of 5yrs must be endorsed by India Limited, at all leves and heigths as per direction of engineer in charge. | Sqm | 189.2
28 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete (IN EXECUTIVE DINNING AREA) | Sqm | 500
TOTAL SUB HEAD
ROLLER BLINDS
29 | Supplying and installing roller blinds of approved make & approved shade at all heights and location and required width and comprising of approved shade and quality fabric, 1 mm thick anodized extruded Aluminium alloy roller tube of 32mm -38mmO.D or 47mm O.D for motorized blinds, a bidirectional operating Clutch mechanism designed for adjustment-free, slippage-free, crash proof smooth operation for all heights, high strength fiber glass reinforced polyester idler, powder coated steel Insert type brackets fitted with roller tube, round bottom rail, control unit engrooved with a Ball Pitch of minimum 6.5mm, plastic Ball Chain, and powder coated atomized steel installation brackets. The clutch mechanism comprises of a plastic beaded chain and carbon steel spring wrapped by means of a high strength fiber glass reinforced polyester assembly to transmit motion from driving to driven members. The installation brackets shall facilitate overhead, side or face mounting with clutch assembly on either end of the roller. Idler shall consist of a centre shaft and outside sleeve which provide bearing surface for roller tube and rotate freely on centre shaft for smooth and quiet operation ( Chain to be provided for Manual blinds only )
Bottom rail along with the fabric shall be enclosed in a suitably created pocket and shall be of powder coated aluminium tube and closed from sides with end caps. The item includes all fittings, accessories, brackets, screws, anchor fasteners, fabric as per approved sample and shade all complete as per drawings, tender specifications, relevant standards and direction of Engineer in charge. (Height of blind from top bracket to bottom tube and width from bracket to bracket shall be measured for payment).
30 | Blackout fabric having following specifications: Composition : Fiberglass with PVC coated or equivalent. washable Openness factor : opaque Weight : min 400 g/sqm Thickness : min 0.36mm Fire Classification : NFPA-701 or equivalent Fastness to light : 5-6 or higher Indoor Air Quality : GreenGuard / Eco-Codice Certified. | Sqm | 400.0008
31 | Screen fabric having following specifications: Composition : 25% (Max) Polyester + 75% (Min) PVC Openness factor : Approx 5% Thickness : 0.56 ± 5% mm Weight : 445 ± 5% g/m2 Fire resistance : Class A NFPA 701 or equivalent Color fastness : 6-7/8 or higher or equivalent Health/Safety certificate : Oekotex /GreenGuard | Sqm | 133.3336
TOTAL SUB HEAD
FALSE CEILING WORKS
32 | LAMINATE WOODEN CEILING (Dinning Hall) Providing and laying custom made wooden false ceiling made of 1 mm thick laminate of approved shade pasted over 12 mm marine plywood of using chemical adhesive including forming grooves as shown with system supported in painted structural steel frame work of planum and vertical hangers angles 25x50x5 mm duly fixed to ceiling using expansion bolts. Lockable cut outs/trap doors and frames shall be provided in false ceilings as per approved design of services. | Sqm | 137.0274
33 | METAL BAFFLE Supply & Fixing of slotted angle-based U-Baffle Ceiling System, comprising of baffle width of 50 mm and height of 150 mm manufactured out of 0.6 mm thick Coil Coated Aluminium of alloy AA 3105 at a module of 200 mm. The coil is coated on a continuous paint line double baked and shall be stove enamelled in a continuous coil coating process with the approved wood finish colour on the exposed side and the reverse side with polyester primer. The coated coil is passed thru ARKU SIX Hi configuration roller levelling process to ensure the flatness of the coil. The baffle shall be manufactured on an integrated high speed, high precision Roll forming machine to avoid micro-cracking of metal corners which occurs while bending on press brake machines. The U Baffle ceiling panels shall be connected using friction grip upper and lower bracket on a primary Steel slotted angle of 30 mm wide x 30 mm high x 2 mm thick with flexible module option of Holes @ 25mm C/C, Black Colour powder coated.The slotted angle shall be suspended with M6 Threaded rod hangers spaced at 1200mm c/c. The length of the panel shall be up to 2400mm. The baffle ceiling system should meet the required standards for Green Pro certification and should qualify as green product as per CII green products and services council. The manufacturer should be ISO 9001:2015. | Sqm | 385.3043
34 | ACOUSTIC PET PANELS (CEILING) Providing & Fixing Acoustical Ceiling with Square edge 20 mm thikness Black Glass Fibre tile easily demountable tile, tile backed with acoustical tissue. Light weight ceiling tiles having NRC upto 0.95 of size 595x595 mm combination of 12.5 mm gypsum board for AC Grills & Diffusers. Which will comprise of density 110 kg/m3 base panel with humidity resistance of 90% RH and light reflectance upto 3-4 % with Leed points Green Performance certified. Black Soft Fibre 15mm for Ceiling tile meet the stringent fire test required having Class ‘A’ rating for Flame Ignitability test as per ASTM-E-84.) to be laid in true horizontal level suspended on inter-locking metal T-Grid of hot dipped galvanised iron section of 0.33mm thick (galvanized @ 120 grams per sqm including both sides) comprising of main-T runners of size 24x32 mm of length 3000 mm, cross - T of size 24x23 mm of length 1200 mm and secondary intermediate cross-T of size 24x23 mm of length 600mm to form grid module of size 600 x 600 mm, suspended from ceiling using galvanised mild steel items (galvanizing @ 80 grams per sqm) i.e. 50 mm long, 8 mm outer diameter M-6 dash fasteners, 6 mm dia fully threaded hanger rod upto 1000 mm length and L-shape level adjuster of size 85x25x2 mm. Galvanised iron perimeter wall angle of size 24x24x0.40 mm of length 3000 mm to be fixed on periphery wall / partition with the help of plastic rawl plugs at 450 mm center to center and 40 mm long dry wall wood screws. The work shall be carried out as per specifications, drawing and as per directions of the Engineer-in-Charge. | Sqm | 92.3115
35 | Providing and fixing in true horizontal level Open cell Aluminium false ceiling system of approved make and shade, comprising of main and secondary blades of width 15 mm and height 37-38mm made of 0.35-0.40mm thick aluminium sheet, cross connected to form 100x100mm square cells to make percentage open are of 72-83%, and laid on the 600mm x 600mm grid system with web height of 38mm per manufacturer's specifications and approved by engineer in charge and shall have sufficient loaded carrying capacity including any additional support members wherever required for light fixtures, AC diffusers, etc. The false ceiling system shall be a noncombustible system. Rate quoted to include all cut outs required for light fixtures, smoke detectors and other services cut outs, all complete as per drawings, manufacturer's specifications and direction of Engineer in Charge. Finished area of false ceiling in horizontal plane and excluding the openings made for 600mm x 600mm size or higher light fittings, diffusers etc shall only be measured for payment. | Sqm | 60
TOTAL SUB HEAD
PAINTING WORKS
36 | Providing and applying of Stucco vapour permeable polished smooth marble finish for interior grade as per approved sample including base coat and primer over smooth POP +putty surface, including cost of surface preparation & scoffolding , all completes as per manufactturer,s specification with the direction of engineer -in - charge . | Sqm | 5
Polishing in high gloss/matt finish melamine clear polish on wood work in required color/wooden shade texture with following process in the sequence as detailed below:
1. The surface to be polished is rubbed with sand paper 80/120 no. and then with sand paper of 160/180 nos
2. Applying two coats of sealer with spray gun and allowing sufficient drying time for 1st coat and 2nd coat is allowed to dry for 8 to 12 hrs.
3. On drying of sealer coat, wet rubbing with emery cloth of finer grading with ample water to remove excess sealer layer and make the surface further smooth after this wet rubbing, then surface is applied with special grade melamine fillers to fill all the small and big holes/grooves etc. Filler coat to be allowed to dry for 4 to 6 hrs on which again a light wet rubbing is done this surface is further allowed to dry for 12 hrs.
| 4. On this, 1st coat of melamine polish is applied with spray gun using melamine clear polish and melamine thinner in required proportion. This 1st coat is allowed to dry for 24 hrs then this dry surface is again fine wet rubbed smooth, which is further allowed to dry for 12 hrs. The final melamine polish is applied with compressor pressure spray gun using melamine clear polish and melamine thinner mixed in required proportion complete as per direction of Engineer-in-Charge. (Final coat to be done in 1 or 2 layers without gap of time.) | Sqm | 5
MR | TEXTURED PAINT Providing & Applying natural Lime blend texture surface of Lime Plaster high gloss by Ultratech Texture Paints or equivalent. The process includes of- One coat of Masionory primer & water in ratio of (1:1) along with repair check with exterior grade putty. •Two coat Lime Plaster Base are to mixed in required shade and consistency with water and to be applied on well dried primer surface with stainless steel trowel. The final top coat consisting of Lime plaster with high buffed ( Grassilo) to be applied on 2st coat of prepared surface to achieve required shade with stainless steel trowel. Finally when well dried surface is ready,it is buffed with stainless steel trowel to obtain desired finish surface. All work to be completed as per direction of engineer -in-charge | Sqm | 401
GLASS RAILING
37 | Providing and fixing stainless steel ( Grade 304) railing made of Hollow tubes, channels, plates etc., including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete, i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in charge, (for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.). | kg | 25
MR | Extra for providing and fixing 12 mm thick toughened glass of approved make and shade in SS railing including providing and fixing all necessary accessories, fittings, studs , etc of SS 304 grade all, complete as per drawing and direction of Engineer in charge | sqm | 5
SS SIGNAGES
38 | Providing & fixing at all heights and locations Letters made up of Stainless steel, grade 316 of approved make made out of laser cut shape in required design, language & font, including buffing, polishing and fixing by sufficient numbers of fasteners/ high quality chemical tape/ adhesive/fastener of approved make, all complete as per architectural drawings and direction of Engineer in charge.
| letters with depth of 50 mm | Per letter per cm height | 10
| letters with depth of 100 mm | Per letter per cm height | 80
| letters with depth of 150 mm | Per letter per cm height | 40
| letters with depth of 200 mm | Per letter per cm height | 5
39 | Supply & application of Designer texture tile/Glazed /matt/Rigatto finish on walls having dimension & Surface Quality- Thickness 9mm, Sizes available- 4/8 ft and 2/4 ft, Water Absorbtion- Avg. ≤ 0,08%, Individual 0,2%, Modulus of Rupture- Min. 42, Breaking Strength- Minimum 1800, Mohs Hardness of surface- 8, Co-efficient of linear thermal expansionFrom ambient temperature to 1000C- 6 X 10-6 K-1 max, Chemical Properties- Resistance to staining- 4,Resistance to household chemicals and swimming pool salts- Minimum A, Resistance to acids & alkalis-Minimum B ,these tiles shall be fixed using recommended tile adhevive (category Iv/S1) and the joints finished using non shrink epoxy grouts in clour and shade of tiles ,base of 12mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) shall be provided. ( Basic rate Rs.173/sqft) | Sqm | 85
40 | METAL BAFFLE WALL Providing and Fixing of 0.7 mm aluminium ,plain, post coat to any RAL finish- vertical Baffle for fixing on wall Baffle Blade comprising of Metal baffle system with Rectangular horizontol baffle blades made of of Aluminium (Grade AA 3xxx, H14 temper) in coated thickness of 0.7mm ± 0.03mm as per IS:2676 (1981), post coated to solid colour, suitable for architectural finishes and Interior applications, with double grid concealed system and butt joint panels. The baffle width shall be 25mm, height shall be 200mm, length shall be ranging up to 3000mm with a C/C distance of 150mm. The baffles shall have plain unperforated finish with square edge, hook-on edges with suitable upturns. The baffles shall be electrostatically powder coated using RoHS compliant pure polyester powder to achieve coating thickness ranging from 60-80 microns. The powder coating shall pass Salt Spray Test for 750 Hours as per ASTM B117, QUV – A Test for 1000hours as per ASTM G-154 – (Cycle – 1) and Humidity test for 1000hours as per DIN 0017. The powder coating shall have an adhesion of GT0 as per EN ISO 2409. The shade variation across batches shall be delta E<1 using Excite/BYK Gardner instrument and gloss level of 25±5% at 60˚ as per ASTM D523. The grids shall comprise primary U-shaped slotted carrier bars of 120gsm galvanised steel (GI) of 3000mm L x 43mm H x 30mm W x 1.5mm T. Accessories shall include baffle connector (GI), baffle face cover (GI), carrier bar splice (GI), carrier hanger (SS), wall anchor (GI) all complete as per manufacturer’s specifications, tender specifications, drawings and direction of Engineer In charge. | Sqm | 24
41 | ACOUSTIC PET PANELS Slim Sculpt, 1200x2400x9mm Supply and installation of Slim Sculpt, surface embossed polyfibre panels, core-pigmented, high-density, SynthPF rigid panels of size 1200x2400x9mm, volume density 200-210kg/m3, weight 1.8kg/m2 adhered on backer board, square edge magnesite bonded 2mm widepinewood fibre core tiles of size 600x1200x10mm, volume density 400kgs/m3, weight 4kg/m2 installed by using Strut framework system. " Strut framework system includes Strut CC25, fully knurled, sectional thickness 0.55mm, length 3600mm, web 50mm, depth of 25mm and equal flanges 15mm is fastened to wall or framework behind horizontally at every 600mm centres. backer board is installed on the Strut CC25 with suitable fasteners at 600mm centres. Longer edges of the panel should be perpendicular to length of Strut CC25. Stick S7 is adhesive applied on backer board and at rear of Slim Sculpt panel. Prior to installation, ensure surface behind are flat, dry and free from dust or other contaminants and leveled. Slim Sculpt panels are then adhered to backer board behind with Stick S7 adhesive." System is backlined with SynthPF 10x25 held in position with dab spots of Stick S7/ wire mesh (wire mesh not by ). Technical Parameters of finish product "• Fire (Class) – A • Acoustics – NRC Upto 0.8 (for system) • Thermal (W/mk)– 0.04 • Climate (°C, RH) – 50, 99 • Light (%) – print Dependant • Green (VoC, RC %) – Nil, 60" | Sqm | 36
42 | Providing and fixing in wall lining medium density fibre board IS: 14587:1998 marked, with necessary fixing arrangement and screws etc. complete. 18 mm thick. | Sqm | 5
| 25 mm thick. | Sqm | 242.55
MR | Architectural Finishes for Walls, Furniture, Partitions or Any Other Solid Smooth Non-Porous Substrate Providing and fixing of high-quality architectural finish for interior surface decoration, having multilayered construction with a pressure sensitive adhesive and air release channel for bubble free and faster application. The architectural finish solution should be easy to clean, should have good chemical and stain resistance properties. The self-adhesive film should be pre-patterned where base film, printing and overlaminate are fused with each other in multilayer construction, to ensure maximum repeatability in design. The surface of the film should be embossed that provides enriched feel effect with corresponding natural finish. The patterns and finishes of these films should closely resemble to natural substrates to ensure improve aesthetics. The film should be easy to clean using detergent (between pH 5 and 8) diluted in water. The film should have ability to withstand impacts and resist scratches to have better durability. The film should be flexible to facilitate easy application. The film should be applied using pressure with appropriate tools without the use of any glue or fluid. Use of primer for surface preparation and increase in adhesion will be permitted. The thickness of these Architectural finishes should be 200 - 220 microns and it should be resistant to common household staining agents. The film should be RoHS compliant & Phthalate free. It should be Class A/B rated (Most Products have Class A) in terms of fire retardancy properties, when used in Interior Applications as defined by NFPA 101 “Life Safety Code”, Test Method ASTM E84. The film should be compliant as low emitting per CA Specification 01350, tested per CDPH Standard Method V1.1-2010. The film should have ability to withstand impacts and resist scratches for better durability. The durability of the product should range between 5-10 years based on different categories for vertical application. | Sqm | 300
MR | Providing wooden architrave of size for door frame made up of extruded solid foam wooden profile having homogenous fine cellular structure with smooth outer integral skin, minimum 50 mm width and minimum 12 mm thick suitable for fixing to frame. The molding shall be snap fitted in the groove provided in the frame & fixed with wooden solvent adhesive/ cement and self tapping screws (of required size) complete as per direction of Engineer-in-Charge. | metre | 56.2275
| POLYSTYRENE PANELS Providing and fixing at all heights and location, Wall Decorative Polystyrene panelling over 12mm thick marine plywood board fixed by 50 mm long dry wall screws at the spacing of 300 mm c/c to GI base frame of 25mm x 50mm at spacing not exceeding 600 mm c/c bothways, with 12mm galvanized metal screws at 600 mm c/c to the wall, secured to floor, structural support and nearest structural member using galvanized metal screws and wooden/ PVC rawl plugs, including finishing with minimum 12mm thick decorative polystyrene panel of approved pattern and colour using adhesive having VOC less than 50grams/Litre with grooves and all necessary accessories with grooves etc. complete as per manufacturer's specification, drawings and direction of Engineer-In-Charge. Note: The quoted rate shall include all the above operations, making cut outs for electrical conduits, networking boxes etc and openings for services and making the same good.(Basic Rate of Decorative Polystyrene Panel - Rs. 3500/Sqm) | Sqm | 5
| Providing and laying Granite stone flooring in required design and patterns in linear as well as curvilinear portions of the building all complete as per the architectural drawings with 18 mm thick stone slab over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with cement slurry admixed with pigment of matching shade including rubbing, curing and polishing and as directed by the Engineer-in-Charge Granite stone slab Dark Black. Dark Red, White or equivalent, Leather Finish Granite | Sqm | 5
MR | Providing and laying Vitrified tiles in floor in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS:15622, of approved brand & manufacturer, in all colours and shade, laid on 20 mm thick cement mortar 1:4 (1 cement: 4 coarse sand) jointing with grey cement slurry @3.3 kg/sqm including grouting the joints with white cement and matching pigments etc. The tiles must be cut with the zero chipping diamond cutter only . Laying of tiles will be done with the notch trowel, plier, wedge, clips of required thickness, leveling system and rubber mallet for placing the tiles gently and easily.
| Size of Tile 200 x 1200 mm | Sqm | 564.7103
MR | Providing, fabricating and fixing Planter boxes of size 1500mm wide x 450mm deep x 450mm H made out of 19mm marine ply conforming to IS 710, finished with 1mm thick laminate of approved make on both the sides and with 19mm x 10mm thick wood beading on all exposed sides finished with spray enamel paint to give even shade matching to the colour of laminate, all Complete as per drawings, specifications and direction of Engineer-In-Charge. | each | 5
MR | Providing and fixing MS powder coated member to hold the planter fixed with invisible screws to the wall | each | 5
MR | Providing & Fixing CNC CUT 17mm MDF Board with fluted effect on partition wall as per architectural drawing & direction of engineer-incharge. (Basic Rate-110 sft ) | Sqm | 5
MR | Providing & Applying DUCO Paint on MDF board in two or more coat to get uniform shade as per architectural drawing & direction of engineer-in-charge. (Basic Rate 850 per sqm) | Sqm | 5
TOTAL SUB HEAD
TOTAL ALL SUB HEAD

## BOQ (GIRLS HOSTEL)
ITEM NO. | DESCRIPTION OF ITEM | UNIT | QUANTITY (GIRLS HOSTEL) | RATE (INR) | AMOUNT (INR)
CLADDING / WALL LINING WORKS
1 | Providing and fixing 2nd class teak wood corner beading of triangular shape and size 50x50 mm (base and height) moulded to the junction of paneling, edgings, margins etc. fixed in position with rawl plugs, nails etc. as required and priming coat on unexposed surface complete with rubbing, polishing etc. as per the direction of Engineer in Charge. | Meter | 10
2 | Providing and fixing 2nd class teak wood moulded beading of approved shape and size to door, window and partition frames with iron screws, plugs and priming coat on unexposed surface etc. all complete. | Cum | 0.1
Providing and fixing carbon steel galvanised ( minimum coating 5 micron) dash fastener of 10 mm dia double threaded 6.8 grade (yield strength 480 N/mm2), counter sunk head, comprising of 10 mm dia polyamide PA 6 grade sleeve, including drilling of hole in frame , concrete/ masonry, etc. as per direction of Engineer-in-charge.
| 10x120 mm | Each | 25
| 10x140 mm | Each | 25
TOTAL SUB HEAD
PARTITION & PANELLING
3 | Providing and fixing frame work for partitions/ wall lining etc. made of 50x25x1.25mm / as approved, hollow MS tube, placed along the walls, ceiling and floor in a grid pattern with spacing @ 60 cm centre to centre both ways (vertically & horizontally) or at required spacing near opening, with necessary welding at junctions and fixing the frame to wall/ ceiling/ floors with steel dash fasteners of 8 mm dia, 75 mm long bolt, including making provision for opening for doors, windows, electrical conduits, switch boards etc., including providing with two coats of approved steel primer etc. complete, all as per direction of Engineer-in-charge. | kg | 2072.1273
4 | Providing and fixing plain lining with necessary screws/nuts & bolts/ nails, including a coat of approved primer on one face, and fixed on wooden /steel frame work, complete as per direction of Engineer-incharge (Frame work shall be paid for separately).
| 12mm thick BWP Grade Ply | sqm | 10
| 19mm thick BWP Grade Ply | sqm | 10
5 | Providing & Fixing decorative high pressure laminated sheet of plain / wood grain in gloss / matt/ suede finish with high density protective surface layer and reverse side of adhesive bonding quality conforming to IS : 2046 Type S, including cost of adhesive of approved quality.
| 1.0 mm thick ( Basic Rate is Rs. 323.00 / Sqm) | Sqm | 314.7726
6 | Providing and fixing plywood of 4mm thick, one side decorative veneer conforming to IS: 1328 (type-1), for plain lining / cladding with necessary screws, including priming coat on unexposed surface with : MS framework shall be paid separatley.
| Decorative veneer facings of approved manufacture (Basic Cost is Rs.850 / Sqm) | sqm | 5
7 | Providing and fixing plain Gypsum board with necessary screws, including a coat of approved primer on one face, and fixed on GI/steel frame work, complete as per direction of Engineer-incharge (Frame work shall be paid for separately), The boards are to be fixed to the frame work with joints staggered to avoid through cracks, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape,joint finisher as per manufacture's specification and direction of engineer in charge all complete.
| 12.5 mm thick tapered edged plain Gypsum plaster board conforming to IS: 2095: (part I): 2011 (Board with BIS certification marks) | sqm | 5
8 | Providing and fixing 6mm thick lacquered glass of approved make on wall panelling over 12mm thick marine plywood/BWP ply base (conforming to IS : 710) fixed over MS frame work. Glass shall be fixed with clear neutral silicon of make GE winsil 20/ silpruf or DOW CORNING 995 over plywood complete as per detail in drawing and directions of Engineer-in-charge. Plywood cost is included in this item. MS Frame work will be paid separately. | Sqm | 5
9 | Providing and fixing 150 mm high Stainless steel sheet skirting made out of 1.2mm thick Stainless steel sheet SS304 moulded to profile inc sections fixed over 12mm thick marine ply using epoxy adhesives, fixing with screws, rubber beading etc.),polishing etc , cutting, bending, curing etc all complete. | Metre | 5
MR | Providing and fixing 6 mm thick marine plywood (conforming to IS: 710) skirting using epoxy adhesives, fixing with screws, etc on partition wall or required location, including a coat of approved primer on one face, as per drawing and directions of Engineer-in-charge | Sqm | 5
MR | Providing and fixing 8 mm thick marine plywood (conforming to IS: 710) skirting using epoxy adhesives, fixing with screws, etc on partition wall or required location, including a coat of approved primer on one face, as per drawing and directions of Engineer-in-charge | Sqm | 5
10 | Providing and fixing 10 mm thick marine plywood (conforming to IS: 710) skirting using epoxy adhesives, fixing with screws, etc on partition wall or required location, including a coat of approved primer on one face, as per drawing and directions of Engineer-in-charge | Sqm | 5
11 | Providing and fixing 12 mm thick marine plywood (conforming to IS: 710) skirting using epoxy adhesives, fixing with screws, etc on partition wall or required location, including a coat of approved primer on one face, as per drawing and directions of Engineer-in-charge | Sqm | 318.7888
12 | ACOUSTIC FABRIC PANELLING Supply and Installation of Soak Cord, kerfed edge, fabric wrapped magnesite bonded 2mm wide pinewood fibre core panel ,GreenPro certified,of size 600x2400x25mm, with ribbed finish, volume density 400Kgs/m3, weight 10 kg/m2 installed by using Strut framework system with Strut H-Spline. "The Strut framework systems includes Strut CC25 thickness 0.55mm, length 3600mm, knurled web 50mm, depth 25mm and equal flanges 15mm is fastened to wall positioned horizontally in a regular manner at 600mm centres. Strut H-Spline having sectional thickness 2mm and length 2400mm to be fixed perpendicular to the Strut CC25 at 600mm centers. Soak cord, Kerfed edge panels shall then be inserted into the Strut H-Spline along their long edges to perfect fit with staggered short edges. Note: Thickness is for bare panels. Add 4mm for Cord fabric. (Fabric colour as per architect's choice from currently valid swatch card)" The system is backlined with the acoustical infill SynthPF 10x25 adhered on wall with dab spots of Stick S7. Technical Parameters "• Fire (Class) – 1 & P • Acoustics – NRC 0.75 (For 20mm thk C25 mounting) upto 0.8 (for 25mm thk, C25 Mounting) • Thermal (W/mk)– 0.07 • Climate (°C, RH) – 50, 95 • Light (%) – Colour Dependant • Green (VoC, RC %) – Low, 30" | Sqm | 5
13 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/sqm(both side inclusive), consisting of floor and ceiling channel 50 mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete. | Sqm
| 75 mm overall thickness partition with 12.5 mm thick double skin fire rated Glass Reinforced Gypsum (GRG) plaster board conforming to IS: 2095: part 3 (Board with BIS certification marks) | Sqm | 10
MR | Providing and fixing self adhesive type frosted glass film of make or approved equivalent, in required pattern over glass etc. as per drawings, including cleaning the receiving surface of glass etc., all complete as per manufacturer's specification and direction of Engineer in charge, bubble-free installation to be done on clean glass by Authorized Installers of /approved make having Certificate of image license and shall provide Warranty for a period of 5 years, all complete as per direction of Enigneer In Charge |  | 0
| Plain frosted/dusted film | Sqm | 4.4208
| Digitally Printed frosted film | Sqm | 12.0062
MR | Providing & Fixing Film (Shade Number) a flexible cast PVC with Comply™ adhesive intended to cover all type of the surfaces, such as wall covering, fur-niture, fixture, ceiling, doors, elevators, exterior/interior applications. Film – approx. 215 microns (film/adhesive) PVC, cadmium-free. Thickness will vary between designs,Adhesive would be Permanent acrylic adhesive with Comply™ performance & a Liner of PE coated Kraft paper. Contractors payment wouldn't be released until & unless he/she produces orginal warranty letter from the ( ) manufacturer. | Sqm | 4.4208
MR | Providing & fixing Decorative / Privacy Glazing Film with the following features backed by manufacturers MCS warranty of 5 years.The material should consist of a durable polyester with a decorative matte surface, manufactured with a silicone liner to protect clear pressure-sensitive adhesive. Films contain no metals, but so contain infrared-absorbing carbon, metal oxide particles, or both. Film should have nominal thickness of between 3.0 mils and 3.5 mils (0.003 and 0.0035 inches).The film color should be clear, containing no metal coatings or dyed polyesters. 1. Ultraviolet Rejected : Not less than 99 percent. 2. Visible Light Transmission : Not more than 49 percent. 3. Visible Light Rejected: Not less than 19 percent. 4. Solar Heat Reduction: Not less than 14 percent. 5. Shading Coefficient at 90 Degrees (Normal Incidence) (ASTM E 903): Not less than 0.62. Backed by MCS warranty for 5Years from ARCHITECTURAL MARKET DEPARTMENT. | Sqm | 22.1042
MR | Providing & Fixing Digitally reproduced decorative graphics on IJ180C (with controltac & comply feature for direct, bubble-free application on walls) with UV protective matte overlaminate 8520 with a polyethylene-coated paper liner. Customised imagery & the thickness of 2 mil (0.05mm) without adhesive & 3-4mil (0.8-0.10mm) with adhesive, having minimum tensile strength of 5 pounds/inch at 73°F (0.9 kg/cm at 23°C ). the adhesive should be Pressure activated, positionable, with air release channels. MCS warranty of 5yrs must be endorsed by India Limited, at all leves and heigths as per direction of engineer in charge. | Sqm | 4.4208
MR | Providing and fixing beveled edge mirror of superior glass (of approved quality) complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete with powder coating aluminium channel. As directed by Engineer-in-charge. | Sqm | 22.5294
MR | Providing and Fixing of 12mm Aluminium profile in anodised finish in approved colour and shade of L or T shape to be fixed with chemical adhesive. Complete as per drawing to be issued. | Sqm | 100
MR | Providing and fixing 18mm thick polished granite fixed on board/ ply with chemical adhesive as per standard manufacturer or approved by engineer in-charge as per the drawings | Sqm | 61.3305
TOTAL SUB HEAD
FALSE CEILING WORKS
14 | METAL BAFFLE Supply & Fixing of slotted angle-based U-Baffle Ceiling System, comprising of baffle width of 50 mm and height of 150 mm manufactured out of 0.6 mm thick Coil Coated Aluminium of alloy AA 3105 at a module of 200 mm. The coil is coated on a continuous paint line double baked and shall be stove enamelled in a continuous coil coating process with the approved wood finish colour on the exposed side and the reverse side with polyester primer. The coated coil is passed thru ARKU SIX Hi configuration roller levelling process to ensure the flatness of the coil. The baffle shall be manufactured on an integrated high speed, high precision Roll forming machine to avoid micro-cracking of metal corners which occurs while bending on press brake machines. The U Baffle ceiling panels shall be connected using friction grip upper and lower bracket on a primary Steel slotted angle of 30 mm wide x 30 mm high x 2 mm thick with flexible module option of Holes @ 25mm C/C, Black Colour powder coated.The slotted angle shall be suspended with M6 Threaded rod hangers spaced at 1200mm c/c. The length of the panel shall be up to 2400mm. The baffle ceiling system should meet the required standards for Green Pro certification and should qualify as green product as per CII green products and services council. The manufacturer should be ISO 9001:2015. | Sqm | 58.9844
15 | ACOUSTIC PET PANELS (CEILING) Providing & Fixing Acoustical Ceiling with Square edge 20 mm thikness Black Glass Fibre tile easily demountable tile, tile backed with acoustical tissue. Light weight ceiling tiles having NRC upto 0.95 of size 595x595 mm combination of 12.5 mm gypsum board for AC Grills & Diffusers. Which will comprise of density 110 kg/m3 base panel with humidity resistance of 90% RH and light reflectance upto 3-4 % with Leed points Green Performance certified. Black Soft Fibre 15mm for Ceiling tile meet the stringent fire test required having Class ‘A’ rating for Flame Ignitability test as per ASTM-E-84.) to be laid in true horizontal level suspended on inter-locking metal T-Grid of hot dipped galvanised iron section of 0.3 m thick (galvanized @ 120 grams per sqm including both sides) comprising of main-T runners of size 24x32 mm of length 3000 mm, cross - T of size 24x23 mm of length 1200 mm and secondary intermediate cross-T of size 24x23 mm of length 600mm to form grid module of size 600 x 600 mm, suspended from ceiling using galvanised mild steel items (galvanizing @ 80 grams per sqm) i.e. 50 mm long, 8 mm outer diameter M-6 dash fasteners, 6 mm dia fully threaded hanger rod upto 1000 mm length and L-shape level adjuster of size 85x25x2 mm. Galvanised iron perimeter wall angle of size 24x24x0.40 mm of length 3000 mm to be fixed on periphery wall / partition with the help of plastic rawl plugs at 450 mm center to center and 40 mm long dry wall wood screws. The work shall be carried out as per specifications, drawing and as per directions of the Engineer-in-Charge. (Make: Earcons Acoustic , , Armstong) | Sqm | 5
TOTAL SUB HEAD
FLOORING WORKS
16 | Providing and fixing of pre-fabricated sports vinyl flooring of approved make & approved color shade, having resistance to stains & scratches, including cutting the rolls to fit the floor size, providing thermal welding for a seamless floor with uniformity, on a moisture free levelled floor surface using water based adhesive recommended by manufacturer, including all tools and tackles, including under layer foam & door profiles etc , at all levels and heights , all complete, fixing /installation shall be done as per manufacturer recommendations and instructions of the engineer in charge. The flooring shall meet the following technical parameters: Overall Thickness : Minimum 6.2mm Top / Wear Layer thickness : Minimum 0.7mm Weight : Minimum 3.95 Kg/Sqm Performance requirements : Complying to EN 14904 Shock Absorption : > 24% | Sqm | 148.7046
0
TOTAL SUB HEAD
PAINTING WORKS
17 | Providing and applying of Stucco vapour permeable polished smooth marble finish for interior grade as per approved sample including base coat and primer over smooth POP +putty surface, including cost of surface preparation & scoffolding , all completes as per manufactturer,s specification with the direction of engineer -in - charge . | Sqm | 5
Polishing in high gloss/matt finish melamine clear polish on wood work in required color/wooden shade texture with following process in the sequence as detailed below:
1. The surface to be polished is rubbed with sand paper 80/120 no. and then with sand paper of 160/180 nos
2. Applying two coats of sealer with spray gun and allowing sufficient drying time for 1st coat and 2nd coat is allowed to dry for 8 to 12 hrs.
3. On drying of sealer coat, wet rubbing with emery cloth of finer grading with ample water to remove excess sealer layer and make the surface further smooth after this wet rubbing, then surface is applied with special grade melamine fillers to fill all the small and big holes/grooves etc. Filler coat to be allowed to dry for 4 to 6 hrs on which again a light wet rubbing is done this surface is further allowed to dry for 12 hrs.
| 4. On this, 1st coat of melamine polish is applied with spray gun using melamine clear polish and melamine thinner in required proportion. This 1st coat is allowed to dry for 24 hrs then this dry surface is again fine wet rubbed smooth, which is further allowed to dry for 12 hrs. The final melamine polish is applied with compressor pressure spray gun using melamine clear polish and melamine thinner mixed in required proportion complete as per direction of Engineer-in-Charge. (Final coat to be done in 1 or 2 layers without gap of time.) | Sqm | 5
18 | TEXTURED PAINT Providing & Applying natural Lime blend texture surface of Lime Plaster high gloss by Ultratech Texture Paints or equivalent. The process includes of- One coat of Masionory primer & water in ratio of (1:1) along with repair check with exterior grade putty. •Two coat Lime Plaster Base are to mixed in required shade and consistency with water and to be applied on well dried primer surface with stainless steel trowel. The final top coat consisting of Lime plaster with high buffed ( Grassilo) to be applied on 2st coat of prepared surface to achieve required shade with stainless steel trowel. Finally when well dried surface is ready,it is buffed with stainless steel trowel to obtain desired finish surface. All work to be completed as per direction of engineer -in-charge | Sqm | 575.9483
GLASS RAILING
19 | Providing and fixing stainless steel ( Grade 304) railing made of Hollow tubes, channels, plates etc., including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete, i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in charge, (for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.). | kg | 25
MR | Extra for providing and fixing 12 mm thick toughened glass of approved make and shade in SS railing including providing and fixing all necessary accessories, fittings, studs , etc of SS 304 grade all, complete as per drawing and direction of Engineer in charge | sqm | 5
MR | Supply & Installation of 1 mm thick Stainless Steel, Grade-304 sheet cladding pasted using chemical adhesive over 2 layers of 6 mm thick water tight commercial flexi ply fixed over frame of 25x50 mm anticorrosive mild steel lincluding providing grooves as per design in mat/glossy/hairline finish complete | Sqm | 5
19 | Supply & application of Designer texture tile/Glazed /matt/Rigatto finish on walls having dimension & Surface Quality- Thickness 9mm, Sizes available- 4/8 ft and 2/4 ft, Water Absorbtion- Avg. ≤ 0,08%, Individual 0,2%, Modulus of Rupture- Min. 42, Breaking Strength- Minimum 1800, Mohs Hardness of surface- 8, Co-efficient of linear thermal expansionFrom ambient temperature to 1000C- 6 X 10-6 K-1 max, Chemical Properties- Resistance to staining- 4,Resistance to household chemicals and swimming pool salts- Minimum A, Resistance to acids & alkalis-Minimum B ,these tiles shall be fixed using recommended tile adhevive (category Iv/S1) and the joints finished using non shrink epoxy grouts in clour and shade of tiles ,base of 12mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) shall be provided. ( Basic rate Rs.173/sqft) | Sqm | 31.4874
| PROVIDING AND FIXING SECOND CLASS TEAK WOOD - WOODEN BAND OF size 75 X 15 MM with necessary screws on wall, partitons, panelling, wall tiles as per design and drawings. | R/M | 531.4123
MR | POLYSTYRENE PANELS Providing and fixing at all heights and location, Wall Decorative Polystyrene panelling over 12mm thick marine plywood board fixed by 50 mm long dry wall screws at the spacing of 300 mm c/c to GI base frame of 25mm x 50mm at spacing not exceeding 600 mm c/c bothways, with 12mm galvanized metal screws at 600 mm c/c to the wall, secured to floor, structural support and nearest structural member using galvanized metal screws and wooden/ PVC rawl plugs, including finishing with minimum 12mm thick decorative polystyrene panel of approved pattern and colour using adhesive having VOC less than 50grams/Litre with grooves and all necessary accessories with grooves etc. complete as per manufacturer's specification, drawings and direction of Engineer-In-Charge. Note: The quoted rate shall include all the above operations, making cut outs for electrical conduits, networking boxes etc and openings for services and making the same good.(Basic Rate of Decorative Polystyrene Panel - Rs. 3500/Sqm) | Sqm | 4.0163
MR | Providing wooden architrave of size for door frame made up of extruded solid foam wooden profile having homogenous fine cellular structure with smooth outer integral skin, minimum 65 mm width and minimum 18 mm thick suitable for fixing to frame. The molding shall be snap fitted in the groove provided in the frame & fixed with wooden solvent adhesive/ cement and self tapping screws (of required size) complete as per direction of Engineer-in-Charge. | metre | 50.4
| Providing and laying Granite stone flooring in required design and patterns in linear as well as curvilinear portions of the building all complete as per the architectural drawings with 18 mm thick stone slab over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with cement slurry admixed with pigment of matching shade including rubbing, curing and polishing and as directed by the Engineer-in-Charge Granite stone slab Dark Black. Dark Red, White or equivalent, Leather Finish Granite | Sqm | 5
MR | Providing, fabricating and fixing Planter boxes of size 1500mm wide x 450mm deep x 450mm H made out of 19mm marine ply conforming to IS 710, finished with 1mm thick laminate of approved make on both the sides and with 19mm x 10mm thick wood beading on all exposed sides finished with spray enamel paint to give even shade matching to the colour of laminate, all Complete as per drawings, specifications and direction of Engineer-In-Charge. | Sqm | 5
MR | Providing and fixing MS powder coated member to hold the planter fixed with invisible screws to the wall | Sqm | 5
MR | Providing & Fixing CNC CUT 17mm MDF Board with fluted effect on partition wall as per architectural drawing & direction of engineer-incharge. (Basic Rate-110 sft ) | Sqm | 5
MR | Providing & Applying DUCO Paint on MDF board in two or more coat to get uniform shade as per architectural drawing & direction of engineer-in-charge. (Basic Rate 850 per sqm) | Sqm | 5
TOTAL SUB HEAD
TOTALALL SUB HEAD